Figure 1. DC Analogy of pressure (voltage) and current.

Figure 2. Comparison of DC and AC voltage.

Figure 3. AC Analogy of pressure (voltage) and current.

Figure 4. Relationship between apparent, real, and reactive power.

Figure 5. Illustration of rating a load in kVA versus kW.

Figure 6. Single-Phase versus Three-Phase.

Figure 6. Single-Phase versus Three-Phase.

Figure 7. Wye versus Delta Connection.

Table 1. Maximum Load Capacity of Common Circuits [ ].

|  | Voltage (V) | Current (A) | Phase | Max Power (kVA) |
| --- | --- | --- | --- | --- |
| North America | 120 | 15 | 1 phase | 1.4 |
|  | 120 | 20 | 1 phase | 1.9 |
|  | 208 | 20 | 1 phase | 3.3 |
|  | 208 | 30 | 1 phase | 4.9 |
|  | 208 | 20 | 3 phase | 5.7 |
|  | 208 | 30 | 3 phase | 8.6 |
|  | 208 | 60 | 3 phase | 17.2 |
| International | 230 | 10 | 1 phase | 2.3 |
|  | 230 | 20 | 1 phase | 3.7 |
|  | 230 | 32 | 1 phase | 7.4 |
|  | 400 | 16 | 3 phase | 11 |
|  | 400 | 32 | 3 phase | 22 |

Table 2 shows the continuous power capacity in kW at each amperage [ ]. The shaded portion of the table represents the uncommon power levels that are not recommended by design engineers.

Table 2. Recommended Continuous Power Capacities (kW) at Each Amperage [ ].

|  | Single/split phase |  |  | 3-phase |  |
| --- | --- | --- | --- | --- | --- |
| Whip amps | 120V | 208V | 240V | 208V | 415V |
| 20A | 1.9 kW | 3.3 kW | 3.8 kW | 5.8 kW | 11.5kW |
| 30A | 2.9 kW | 5.0 kW | 5.8 kW | 8.6 kW | 17.3 kW |
| 40A | 3.8 kW | 6.7 kW | 7.7 kW | 11.5 kW | 23.0 kW |
| 50A | 4.8 kW | 8.3 kW | 9.6 kW | 14.4 kW | 28.8 kW |
| 60A | 5.8 kW | 10.0 kW | 11.5 kW | 17.3 kW | 34.5 kW |

Figure 9. Comparison Between Using Nameplate Ratings and Actual Measurements.