LED Streetlights

Product Specification

Important Notice

- To reduce the risk of electric shock, disconnect power supply before installation or servicing.

- This luminaire must be installed in accordance with the local electrical code.  If you are not familiar with these codes and requirements, consult a qualified electrician.

- If NEMA photo control is installed refer to NEMA Receptacle section for instructions.

- If mounting bolts are completely removed in the field they should be hand threaded (prior to use of power tools) to ensure proper engagement of the thread when re-installing.  Failure to pre-start threads may result in cross-threading or stripping of the bolts during reinstallation.

- The luminaire is designed for outdoor use only

- The light source contained in this luminaire shall only be replaced by the manufacturer or his service agent or a similarly qualified person.

ELECTRICAL RATINGS:

| Model | Rated Voltage, Vac | Frequency, Hz | Rated Current, Max. A | Rated Wattage, W | Unit Type | Locations Use |
| --- | --- | --- | --- | --- | --- | --- |
| TLXXX-YY-ZZ-U-V-T | 120-277 | 50/60 | 0.45 | 30-45 | Pole mounted | Wet |
| TLXXX-YY-ZZ-U-V-T | 120-277 | 50/60 | 0.65 | 45-65 |  |  |
| TLXXX-YY-ZZ-U-V-T | 120-277 | 50/60 | 0.85 | 65-85 |  |  |
| TLXXX-YY-ZZ-U-V-T | 120-277 | 50/60 | 1.10 | 85-110 |  |  |
| TLXXX-YY-ZZ-U-V-T | 120-277 | 50/60 | 1.30 | 100-130 |  |  |
| TLXXX-YY-ZZ-U-V-T | 120-277 | 50/60 | 1.60 | 125-165 |  |  |
| TLXXX-YY-ZZ-U-V-T | 120-277 | 50/60 | 2.00 | 150-200 |  |  |
| TLXXX-YY-ZZ-U-V-T | 120-277 | 50/60 | 2.50 | 200-250 |  |  |

NOMENCLATURE:

| Example: | TL | 045 | 2M | CW | U | P | G |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Group: | TL | XXX | YY | ZZ | U | V | T |

| Group | Description |
| --- | --- |
| TL | Series name; |
| XXX | Represent lamp wattage, may be any number, e.g. 045=45W; |
| YY | Represent the optics model number; |
| ZZ | Represent color temperature, may be CW - Cool White; NW - Neutral White; WW - Warm White; MW - Mesopic. |
| U | Represents input voltage is 120-277V; |
| V | Represents dimming function, may be P - Photocell; D - DALI; Z - 0-10V. |
| T | Represents lamp color, may be G - Gray; B- Black; W - White. |

LIGHTING DISTRIBUTION TYPES:

Type II Medium

Type III Medium

Type IV Medium

| TL043-YY-ZZ-U-D-T |  |  |  |  |
| --- | --- | --- | --- | --- |
| PERFORMANCE CRITERIA - LED LUMINAIRE |  |  |  |  |
| VOLTAGE | Nominal luminaire input voltage range |  |  | 120-277 V |
| INPUT POWER | Nominal luminaire input power |  |  | 43 W |
| LUMEN OUTPUT | Min. luminaire lumen output |  |  |  |
| EFFICACY | Min. maintained luminaire efficacy at 3000K |  |  |  |
| POWER FACTOR | Min. power factor |  |  | 0.90 |
| LUMEN MAINT. | Min. % of the initial output at 85,000 hours operation |  |  | L80=88,500 H |
| LMF | Min. Calculated Luminaire Maintenance Factor |  |  | 0.80 |
| CHROMATICITY SHIFT | Max. LED chromaticity shift at 6,000 hours operation |  |  | 0.002 Duv |
| NOMINAL CCT | Nominal correlated color temperature |  |  | 3000K / 4000K |
| CRI | Color Rendering Index |  |  | >70 |
| WEIGHT | Max. luminaire weight |  |  | 18.2 lbs. |
| SAIL AREA | Max. effective sail area |  |  | 0.80 ft2 |
| TERMINAL BLOCK | 6-Way Screw Down Terminal Blocks |  |  | 6AWG-14AWG |
| PCR | Photoelectric Control Receptacle |  |  | Tool-less rotatable |
| MOUNTING SLIPFITTER | Top-entry | Side-entry | Integral tilt (-10° to +10°) |  |
|  | Nominal pole size (NPS) |  |  | 1.25”/2” |
| OPTICAL DISTRIBUTION | Type II | Type III | Type IV | Type V |
| VIBRATION | ANSI C136.31 | Level 1 (normal) | Level 2 (bridge/overpass) |  |
| THERMAL ENVIRONMENT | Typical min. ambient temperature during operation |  |  | -30 °C |
|  | Typical max. ambient temperature during operation |  |  | +50 °C |
| SURGE PROTECTION DEVICE | ANSI C136.2 | Basic (6kV / 3kA) | Enhanced (10kV / 5kA) | Elevated, (20kV / 10kA) |
| CONTROL INTERFACE | None | ANSI C136.10, 3-pin | ANSI C136.41, 5-pin | ANSI C136.41, 7-pin |
| LED DRIVER | Not dimmable | Dimmable, 0-10V (IEC 60929) |  | Dimmable, DALI (IEC 62386) |
| CERTIFICATIONS - LED LUMINAIRE |  |  |  |  |
| SAFETY | UL 1598, UL 8750 |  |  | USL Certified |
| SAFETY | CSA C22.2 No. 250.0, CSA C22.2 No. 250.13 |  |  | CNL Certified |
| FCC | 47 CFR Part 15 Subpart B |  |  | FCC Certified |
| DIELECTRIC WITHSTAND AND ELECTRICAL TRANSIENT IMMUNITY | C136.2-2015: Clause 6, Clause 7, 7.1, 7.2, 7.3, 7.4 |  |  | Certified |
| INGRESS PROTECTION | Ingress protection |  |  | IP65 |
| THD | Max. Total Harmonic Distortion (%) |  |  | 20 |
| IMPACT TEST | Resistance to external mechanical impact test |  |  | IK08 |
| SALINE MIST TEST | Salt spray test to ISO 9227 |  |  | 1,000 hours |
| PHOTOBIO. SAFETY | EN 62471 |  |  | Exempt group |
| PHOTOBIO. SAFETY | EN 62778 |  |  | Risk group 1 |
| RoHS COMPLIANCE | European Directive 2011/65/EC |  |  | SGS Certified |
| MATERIAL - LED LUMINAIRE |  |  |  |  |
| OPTICAL MATERIAL | Optical lens material |  |  | UVC-Polycarbonate |
| HOUSING MATERIAL | Die-cast Aluminum alloy |  |  | 6063 |
| FINISH | Polyester powder coating |  |  | Upon request |

Photos for one-module luminaire: “TL043-YY-ZZ-U-D-T”

| TL085-YY-ZZ-U-D-T |  |  |  |  |
| --- | --- | --- | --- | --- |
| PERFORMANCE CRITERIA - LED LUMINAIRE |  |  |  |  |
| VOLTAGE | Nominal luminaire input voltage range |  |  | 120-277 V |
| INPUT POWER | Nominal luminaire input power |  |  |  |
| LUMEN OUTPUT | Min. luminaire lumen output |  |  |  |
| EFFICACY | Min. maintained luminaire efficacy at 3000K |  |  |  |
| POWER FACTOR | Min. power factor |  |  | 0.90 |
| LUMEN MAINT. | Min. % of the initial output at 85,000 hours operation |  |  | L80=88,500 H |
| LMF | Min. Calculated Luminaire Maintenance Factor |  |  | 0.80 |
| CHROMATICITY SHIFT | Max. LED chromaticity shift at 6,000 hours operation |  |  | 0.002 Duv |
| NOMINAL CCT | Nominal correlated color temperature |  |  | 3000K / 4000K |
| CRI | Color Rendering Index |  |  | >70 |
| WEIGHT | Max. luminaire weight |  |  | 18.2 lbs. |
| SAIL AREA | Max. effective sail area |  |  | 0.80 ft2 |
| TERMINAL BLOCK | 6-Way Screw Down Terminal Blocks |  |  | 6AWG-14AWG |
| PCR | Photoelectric Control Receptacle |  |  | Tool-less rotatable |
| OPTICAL DISTRIBUTION | Type II | Type III | Type IV | Type V |
| MOUNTING SLIPFITTER | Top-entry | Side-entry | Integral tilt (-10° to +10°) |  |
|  | Nominal pole size (NPS) |  |  | 1.25”/2” |
| VIBRATION | ANSI C136.31 | Level 1 (normal) | Level 2 (bridge/overpass) |  |
| THERMAL ENVIRONMENT | Typical min. ambient temperature during operation |  |  | -30 °C |
|  | Typical max. ambient temperature during operation |  |  | +50 °C |
| SURGE PROTECTION DEVICE | ANSI C136.2 | Basic (6kV / 3kA) | Enhanced (10kV / 5kA) | Elevated, (20kV / 10kA) |
| CONTROL INTERFACE | None | ANSI C136.10, 3-pin | ANSI C136.41, 5-pin | ANSI C136.41, 7-pin |
| LED DRIVER | Not dimmable | Dimmable, 0-10V (IEC 60929) |  | Dimmable, DALI (IEC 62386) |
| CERTIFICATIONS - LED LUMINAIRE |  |  |  |  |
| SAFETY | UL 1598, UL 8750 |  |  | USL Certified |
| SAFETY | CSA C22.2 No. 250.0, CSA C22.2 No. 250.13 |  |  | CNL Certified |
| FCC | 47 CFR Part 15 Subpart B |  |  | FCC Certified |
| DIELECTRIC WITHSTAND AND ELECTRICAL TRANSIENT IMMUNITY | C136.2-2015: Clause 6, Clause 7, 7.1, 7.2, 7.3, 7.4 |  |  | Certified |
| INGRESS PROTECTION | Ingress protection |  |  | IP65 |
| THD | Max. Total Harmonic Distortion (%) |  |  | 20 |
| IMPACT TEST | Resistance to external mechanical impact test |  |  | IK08 |
| SALINE MIST TEST | Salt spray test to ISO 9227 |  |  | 1,000 hours |
| PHOTOBIO. SAFETY | EN 62471 |  |  | Exempt group |
| PHOTOBIO. SAFETY | EN 62778 |  |  | Risk group 1 |
| RoHS COMPLIANCE | European Directive 2011/65/EC |  |  | SGS Certified |
| MATERIAL - LED LUMINAIRE |  |  |  |  |
| OPTICAL MATERIAL | Optical lens material |  |  | UVC-Polycarbonate |
| HOUSING MATERIAL | Die-cast Aluminum alloy |  |  | 6063 |
| FINISH | Polyester powder coating |  |  | Upon request |

Photos for one-module luminaire: “TL085-YY-ZZ-U-D-T”

| TL132-YY-ZZ-U-D-T |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| PERFORMANCE CRITERIA - LED LUMINAIRE |  |  |  |  |  |
| VOLTAGE | Nominal luminaire input voltage range |  |  |  | 120-277 V |
| INPUT POWER | Nominal luminaire input power |  |  |  |  |
| LUMEN OUTPUT | Min. luminaire lumen output |  |  |  |  |
| EFFICACY | Min. maintained luminaire efficacy at 3000K |  |  |  |  |
| POWER FACTOR | Min. power factor |  |  |  | 0.90 |
| LUMEN MAINT. | Min. % of the initial output at 85,000 hours operation |  |  |  | L80=88,500 H |
| LMF | Min. Calculated Luminaire Maintenance Factor |  |  |  | 0.80 |
| CHROMATICITY SHIFT | Max. LED chromaticity shift at 6,000 hours operation |  |  |  | 0.002 Duv |
| NOMINAL CCT | Nominal correlated color temperature |  |  |  | 3000K / 4000K |
| CRI | Color Rendering Index |  |  |  | >70 |
| WEIGHT | Max. luminaire weight |  |  |  | 22.2 lbs. |
| SAIL AREA | Max. effective sail area |  |  |  | 0.93 ft2 |
| TERMINAL BLOCK | 6-Way Screw Down Terminal Blocks |  |  |  | 6AWG-14AWG |
| PCR | Photoelectric Control Receptacle |  |  |  | Tool-less rotatable |
| OPTICAL DISTRIBUTION | Type II | Type III | Type IV |  | Type V |
| MOUNTING SLIPFITTER | Top-entry | Side-entry | Integral tilt (-10° to +10°) |  |  |
|  | Nominal pole size (NPS) |  |  |  | 1.25”/2” |
| VIBRATION | ANSI C136.31 | Level 1 (normal) |  | Level 2 (bridge/overpass) |  |
| THERMAL ENVIRONMENT | Typical min. ambient temperature during operation |  |  |  | -30 °C |
|  | Typical max. ambient temperature during operation |  |  |  | +50 °C |
| SURGE PROTECTION DEVICE | ANSI C136.2 | Basic (6kV / 3kA) | Enhanced (10kV / 5kA) |  | Elevated, (20kV / 10kA) |
| CONTROL INTERFACE | None | ANSI C136.10, 3-pin | ANSI C136.41, 5-pin |  | ANSI C136.41, 7-pin |
| LED DRIVER | Not dimmable | Dimmable, 0-10V (IEC 60929) |  |  | Dimmable, DALI (IEC 62386) |
| CERTIFICATIONS - LED LUMINAIRE |  |  |  |  |  |
| SAFETY | UL 1598, UL 8750 |  |  |  | USL Certified |
| SAFETY | CSA C22.2 No. 250.0, CSA C22.2 No. 250.13 |  |  |  | CNL Certified |
| FCC | 47 CFR Part 15 Subpart B |  |  |  | FCC Certified |
| DIELECTRIC WITHSTAND AND ELECTRICAL TRANSIENT IMMUNITY | C136.2-2015: Clause 6, Clause 7, 7.1, 7.2, 7.3, 7.4 |  |  |  | Certified |
| INGRESS PROTECTION | Ingress protection |  |  |  | IP65 |
| THD | Max. Total Harmonic Distortion (%) |  |  |  | 20 |
| IMPACT TEST | Resistance to external mechanical impact test |  |  |  | IK08 |
| SALINE MIST TEST | Salt spray test to ISO 9227 |  |  |  | 1,000 hours |
| PHOTOBIO. SAFETY | EN 62471 |  |  |  | Exempt group |
| PHOTOBIO. SAFETY | EN 62778 |  |  |  | Risk group 1 |
| RoHS COMPLIANCE | European Directive 2011/65/EC |  |  |  | SGS Certified |
| MATERIAL - LED LUMINAIRE |  |  |  |  |  |
| OPTICAL MATERIAL | Optical lens material |  |  |  | UVC-Polycarbonate |
| HOUSING MATERIAL | Die-cast Aluminum alloy |  |  |  | 6063 |
| FINISH | Polyester powder coating |  |  |  | Upon request |

Photos for two-module luminaire: “TL132-YY-ZZ-U-D-T”

| TL190-YY-ZZ-U-D-T |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| PERFORMANCE CRITERIA - LED LUMINAIRE |  |  |  |  |  |
| VOLTAGE | Nominal luminaire input voltage range |  |  |  | 120-277 V |
| INPUT POWER | Nominal luminaire input power |  |  |  |  |
| LUMEN OUTPUT | Min. luminaire lumen output |  |  |  |  |
| EFFICACY | Min. maintained luminaire efficacy at 3000K |  |  |  |  |
| POWER FACTOR | Min. power factor |  |  |  | 0.90 |
| LUMEN MAINT. | Min. % of the initial output at 85,000 hours operation |  |  |  | L80=88,500 H |
| LMF | Min. Calculated Luminaire Maintenance Factor |  |  |  | 0.80 |
| CHROMATICITY SHIFT | Max. LED chromaticity shift at 6,000 hours operation |  |  |  | 0.002 Duv |
| NOMINAL CCT | Nominal correlated color temperature |  |  |  | 3000K / 4000K |
| CRI | Color Rendering Index |  |  |  | >70 |
| WEIGHT | Max. luminaire weight |  |  |  | 26.1 lbs. |
| SAIL AREA | Max. effective sail area |  |  |  | 1.07 ft2 |
| TERMINAL BLOCK | 6-Way Screw Down Terminal Blocks |  |  |  | 6AWG-14AWG |
| PCR | Photoelectric Control Receptacle |  |  |  | Tool-less rotatable |
| OPTICAL DISTRIBUTION | Type II | Type III | Type IV |  | Type V |
| MOUNTING SLIPFITTER | Top-entry | Side-entry | Integral tilt (-10° to +10°) |  |  |
|  | Nominal pole size (NPS) |  |  |  | 1.25”/2” |
| VIBRATION | ANSI C136.31 | Level 1 (normal) |  | Level 2 (bridge/overpass) |  |
| THERMAL ENVIRONMENT | Typical min. ambient temperature during operation |  |  |  | -30 °C |
|  | Typical max. ambient temperature during operation |  |  |  | +50 °C |
| SURGE PROTECTION DEVICE | ANSI C136.2 | Basic (6kV / 3kA) | Enhanced (10kV / 5kA) |  | Elevated, (20kV / 10kA) |
| CONTROL INTERFACE | None | ANSI C136.10, 3-pin | ANSI C136.41, 5-pin |  | ANSI C136.41, 7-pin |
| LED DRIVER | Not dimmable | Dimmable, 0-10V (IEC 60929) |  |  | Dimmable, DALI (IEC 62386) |
| CERTIFICATIONS - LED LUMINAIRE |  |  |  |  |  |
| SAFETY | UL 1598, UL 8750 |  |  |  | USL Certified |
| SAFETY | CSA C22.2 No. 250.0, CSA C22.2 No. 250.13 |  |  |  | CNL Certified |
| FCC | 47 CFR Part 15 Subpart B |  |  |  | FCC Certified |
| DIELECTRIC WITHSTAND AND ELECTRICAL TRANSIENT IMMUNITY | C136.2-2015: Clause 6, Clause 7, 7.1, 7.2, 7.3, 7.4 |  |  |  | Certified |
| INGRESS PROTECTION | Ingress protection |  |  |  | IP65 |
| THD | Max. Total Harmonic Distortion (%) |  |  |  | 20 |
| IMPACT TEST | Resistance to external mechanical impact test |  |  |  | IK08 |
| SALINE MIST TEST | Salt spray test to ISO 9227 |  |  |  | 1,000 hours |
| PHOTOBIO. SAFETY | EN 62471 |  |  |  | Exempt group |
| PHOTOBIO. SAFETY | EN 62778 |  |  |  | Risk group 1 |
| RoHS COMPLIANCE | European Directive 2011/65/EC |  |  |  | SGS Certified |
| MATERIAL - LED LUMINAIRE |  |  |  |  |  |
| OPTICAL MATERIAL | Optical lens material |  |  |  | UVC-Polycarbonate |
| HOUSING MATERIAL | Die-cast Aluminum alloy |  |  |  | 6063 |
| FINISH | Polyester powder coating |  |  |  | Upon request |

| TL250-YY-ZZ-U-D-T |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| PERFORMANCE CRITERIA - LED LUMINAIRE |  |  |  |  |  |
| VOLTAGE | Nominal luminaire input voltage range |  |  |  | 120-277 V |
| INPUT POWER | Nominal luminaire input power |  |  |  |  |
| LUMEN OUTPUT | Min. luminaire lumen output |  |  |  |  |
| EFFICACY | Min. maintained luminaire efficacy at 3000K |  |  |  |  |
| POWER FACTOR | Min. power factor |  |  |  | 0.90 |
| LUMEN MAINT. | Min. % of the initial output at 85,000 hours operation |  |  |  | L80=88,500 H |
| LMF | Min. Calculated Luminaire Maintenance Factor |  |  |  | 0.80 |
| CHROMATICITY SHIFT | Max. LED chromaticity shift at 6,000 hours operation |  |  |  | 0.002 Duv |
| NOMINAL CCT | Nominal correlated color temperature |  |  |  | 3000K / 4000K |
| CRI | Color Rendering Index |  |  |  | >70 |
| WEIGHT | Max. luminaire weight |  |  |  | 30.1 lbs. |
| SAIL AREA | Max. effective sail area |  |  |  | 1.19 ft2 |
| TERMINAL BLOCK | 6-Way Screw Down Terminal Blocks |  |  |  | 6AWG-14AWG |
| PCR | Photoelectric Control Receptacle |  |  |  | Tool-less rotatable |
| OPTICAL DISTRIBUTION | Type II | Type III | Type IV |  | Type V |
| MOUNTING SLIPFITTER | Top-entry | Side-entry | Integral tilt (-10° to +10°) |  |  |
|  | Nominal pole size (NPS) |  |  |  | 1.25”/2” |
| VIBRATION | ANSI C136.31 | Level 1 (normal) |  | Level 2 (bridge/overpass) |  |
| THERMAL ENVIRONMENT | Typical min. ambient temperature during operation |  |  |  | -30 °C |
|  | Typical max. ambient temperature during operation |  |  |  | +50 °C |
| SURGE PROTECTION DEVICE | ANSI C136.2 | Basic (6kV / 3kA) | Enhanced (10kV / 5kA) |  | Elevated, (20kV / 10kA) |
| CONTROL INTERFACE | None | ANSI C136.10, 3-pin | ANSI C136.41, 5-pin |  | ANSI C136.41, 7-pin |
| LED DRIVER | Not dimmable | Dimmable, 0-10V (IEC 60929) |  |  | Dimmable, DALI (IEC 62386) |
| CERTIFICATIONS - LED LUMINAIRE |  |  |  |  |  |
| SAFETY | UL 1598, UL 8750 |  |  |  | USL Certified |
| SAFETY | CSA C22.2 No. 250.0, CSA C22.2 No. 250.13 |  |  |  | CNL Certified |
| FCC | 47 CFR Part 15 Subpart B |  |  |  | FCC Certified |
| DIELECTRIC WITHSTAND AND ELECTRICAL TRANSIENT IMMUNITY | C136.2-2015: Clause 6, Clause 7, 7.1, 7.2, 7.3, 7.4 |  |  |  | Certified |
| INGRESS PROTECTION | Ingress protection |  |  |  | IP65 |
| THD | Max. Total Harmonic Distortion (%) |  |  |  | 20 |
| IMPACT TEST | Resistance to external mechanical impact test |  |  |  | IK08 |
| SALINE MIST TEST | Salt spray test to ISO 9227 |  |  |  | 1,000 hours |
| PHOTOBIO. SAFETY | EN 62471 |  |  |  | Exempt group |
| PHOTOBIO. SAFETY | EN 62778 |  |  |  | Risk group 1 |
| RoHS COMPLIANCE | European Directive 2011/65/EC |  |  |  | SGS Certified |
| MATERIAL - LED LUMINAIRE |  |  |  |  |  |
| OPTICAL MATERIAL | Optical lens material |  |  |  | UVC-Polycarbonate |
| HOUSING MATERIAL | Die-cast Aluminum alloy |  |  |  | 6063 |
| FINISH | Polyester powder coating |  |  |  | Upon request |

Photos for four-module luminaire: “TL250-YY-ZZ-U-D-T”

Weight and Dimension

| Model | Module Quantity | Weight (lbs.) | Dimension (L x W x H) (in) | Sailing Area (ft2) |
| --- | --- | --- | --- | --- |
| TL043-YY-ZZ-U-D-T | 1 | 18.2 | 21.5 x 11.4 x 5.3 | 0.80 |
| TL085-YY-ZZ-U-D-T | 1 | 18.2 | 21.5 x 11.4 x 5.3 | 0.80 |
| TL132-YY-ZZ-U-D-T | 2 | 22.2 | 25.1 x 11.4 x 5.3 | 0.93 |
| TL190-YY-ZZ-U-D-T | 3 | 26.1 | 28.7 x 11.4 x 5.3 | 1.07 |
| TL250-YY-ZZ-U-D-T | 4 | 30.1 | 32.4 x 11.4 x 5.3 | 1.19 |

Remark:

*       Different color temperature is available upon request.

**     For other pole diameters, a different mounting adaptor is required.